## vacuum
Name of Facility: | [59 empty] | VACUUM
pressure drop in "Hg per 100 ft of pipe
Project Number:
[60 empty] | SCFM | 3/4" | 1" | 1 1/4" | 1 1/2" | 2" | 2 1/2" | 3" | 4"
ENTER REQUIRED DATA IN THE BLUE SHADED AREAS BELOW | [59 empty] | 5 | 1.8 | 0.44 | 0.14 | 0.07 |  |  |  |  | #N/A | #N/A | #N/A |  | branch 1 | branch 2 | branch 3
[60 empty] | 10 | 10 | 1.4 | 0.46 | 0.22 | 0.06 |  |  |  | #N/A | #N/A | #N/A | CFM: | 0 | 0 | 0
LOCATION OF OUTLETS |  | VACUUM | [57 empty] | 15 | 10 | 2.7 | 0.9 | 0.42 | 0.115 |  |  |  | #N/A | #N/A | #N/A | length (ft): | 0 | 0 | 0
|  | Outlet Q'ty | Free Air Allowance, SCFM |  |  | Simultaneous | Number of Beds, | Vacuum | [51 empty] | 20 | 10 | 2 | 1.5 | 0.725 | 0.195 | 0.065
|  | per location | Per Bed | Per Room | Per Outlet | use Factor | Rooms or Outlets | SCFM | [51 empty] | 25 | 10 | 3 | 2.25 | 1.1 | 0.3 | 0.1 | [5 empty] | pipe dia:
Anesthetizing Locations | [59 empty] | 30 | 10 | 10 | 3.15 | 1.55 | 0.41 | 0.14 | 0.06
[27 empty] | recommended | alternate | alternate | alternate |  | total |  |  |  | amps | noise | [7 empty] | recommended | alternate | alternate | alternate |  | total |  |  |  | amps | noise |  |  |  |  | 35 | 10 | 10 | 10 | 2 | 0.54 | 0.18 | 0.0775 | [5 empty] | #DIV/0! | #DIV/0! | #DIV/0!
1 | Operating Room | 3/Room |  | 3.5 |  | 100 | 0 | 0 | [8 empty] | Altitude Compensation | [8 empty] | scfm | model # | model # | model # | model # | desc | usage | Hp | Btu/h | sys cap | 208/460 | level | dims | alt 1 dims | alt 2 dims | alt 3 dims |  |  | scfm | model # | model # | model # | model # | desc | usage | Hp | Btu/h | sys cap | 208/460 | level | dims | alt 1 dims | alt 2 dims | alt 3 dims | 40 | 10 | 10 | 10 | 2.5 | 0.675 | 0.23 | 0.0975 | [5 empty] | = 2" x 100 ft x 1.2
2 | Cystoscopy | 3/Room |  | 2 |  | 100 | 0 | 0 | [8 empty] | feet | mult | "HgA |  |  |  |  | 525 | 3 | 3 | V-RVL-D-080P-TS-N-010 | V-RVL-D-080P-TS-N-010 |  |  | Duplex, 1 Hp | 10 | 1 | 2040 | 5.1 | 3.5/1.6 | 58 | 34 x 38 x 68 | 63 x 30 x 40 |  |  | 165 | 2 | 2 | V-RVD-D-080P-TS-N-010 | V-RVD-D-080P-TH-N-010 |  |  | Duplex, 1 Hp | 10 | 1 | 2040 | 3 | 3.9/2.25 | 64 | 32 x 38 x 67 | 66 x 34 x 45 |  |  | 45 | 10 | 10 | 10 | 3 | 0.825 | 0.28 | 0.12 | [5 empty] | length (ft) x 1.4
3 | Delivery | 3/Room |  | 1 |  | 100 | 0 | 0 | [7 empty] | 0 | 0 | 1 | 29.92 |  |  |  |  | 330 | V-RVL-D-080P-TS-N-010 | 5 | V-RVL-D-080P-TS-N-015 | V-RVL-D-080P-TS-N-015 |  |  | Duplex, 1.5 Hp | 10 | 1.5 | 3050 | 7.4 | 5.3/2.5 | 59 | 34 x 38 x 68 | 63 x 35 x 40 |  |  | 100 | V-RVD-D-080P-TS-N-010 | 4 | V-RVD-D-080P-TS-N-015 | V-RVD-D-080P-TH-N-015 |  |  | Duplex, 1.5 Hp | 10 | 1.5 | 3050 | 4.8 | 6/3.5 | 67 | 32 x 38 x 67 | 66 x 34 x 45 |  |  | 50 | 10 | 10 | 10 | 3.6 | 0.975 | 0.33 | 0.14
4 | Special proced. (Open | [14 empty] | 1 | 500 | 1.0192 | 29.6 |  |  |  |  | 280 | Duplex, 1 Hp | 9 | V-RVL-D-120P-TS-N-020 | V-RVL-D-080P-TH-N-020 |  |  | Duplex, 2 Hp | 50 | 2 | 4580 | 12.4 | 6.5/3.1 | 63 | 44 x 44 x 70 | 63 x 37 x 40 |  |  | 50 | Duplex, 1 Hp | 7 | V-RVD-D-080P-TS-N-020 | V-RVD-D-080P-TH-N-020 |  |  | Duplex, 2 Hp | 10 | 2 | 4070 | 8.1 | 6.9/3.6 | 72 | 32 x 38 x 67 | 66 x 34 x 46 |  |  | 60 | 10 | 10 | 10 | 10 | 1.35 | 0.45 | 0.195 | 0.0525
| Heart, Transplant, etc.) | 3/Room |  | 4 |  | 100 | 0 | 0 | [8 empty] | 1000 | 1.0584 | 29 |  |  |  |  | 219 | 10 | 12 | V-RVL-D-120P-TS-N-030 | V-RVL-D-120P-TH-N-030 |  |  | Duplex, 3 Hp | 50 | 3 | 6870 | 17.3 | 8.5/4.1 | 65 | 44 x 44 x 70 | 69 x 39 x 45 |  |  | 23 | 10 | 10 | V-RVD-D-080P-TS-N-030 | V-RVD-D-120P-TL-N-030 |  |  | Duplex, 3 Hp | 50 | 3 | 6110 | 12 | 8.8/4.8 | 76 | 34 x 39 x 78 | 72 x 40 x 58 |  |  | 70 | 10 | 10 | 10 | 10 | 1.8 | 0.6 | 0.26 | 0.07 |  |  |  |  | zone 1 | zone 2 | zone 3 | zone 4 | zone 5 | zone 6 | zone 7 | zone 8 | zone 9 | zone 10
5 | Emergency / Major | [15 empty] | 1500 | 1.0949 | 28.5 |  |  |  |  | 140 | 1 | 19 | V-RVL-D-120P-TS-N-050 | V-RVL-D-120P-TH-N-050 |  |  | Duplex, 5 Hp | 50 | 5 | 11450 | 27.5 | 15.0/6.0 | 69 | 44 x 45 x 73 | 69 x 41 x 47 |  |  | 16 | 1 | 16 | V-RVD-D-120P-TS-N-050 | V-RVD-D-120P-TH-N-050 |  |  | Duplex, 5 Hp | 50 | 5 | 10180 | 21.2 | 14.2/6.4 | 77 | 44 x 44 x 72 | 72 x 41 x 58 |  |  | 80 | 10 | 10 | 10 | 10 | 2.3 | 0.775 | 0.34 | 0.09 |  |  |  | CFM: | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Trauma Room | 3/Room |  | 3 |  | 100 | 0 | 0 | [8 empty] | 2000 | 1.1355 | 28 |  |  |  |  | 70 | 2040 | 26 | V-RVL-D-120P-TS-N-050 | V-RVL-D-120P-TL-N-050 |  |  | Duplex, 5 Hp | 50 | 5 | 12090 | 37.3 | 15.0/6.0 | 71 | 44 x 45 x 73 | 69 x 42 x 47 |  |  | 10 | 2040 | 23 | V-RVD-D-120P-TS-N-075 | V-RVD-D-200P-TL-N-075 | V-RVD-D-120P-SS-N-075 |  | Duplex, 7.5 Hp | 50 | 7.5 | 15270 | 29 | 20.1/9.7 | 79 | 43 x 45 x 83 | 72 x 45 x 65 | 54 x 45 x 86 |  | 90 | 10 | 10 | 10 | 10 | 2.9 | 0.975 | 0.42 | 0.115 |  |  |  | length (ft): | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | Other Anesthetizing | [15 empty] | 2500 | 1.1713 | 27.6 |  |  |  |  | 60 | 3.5/1.6 | 34 | V-RVL-D-200P-TS-N-075 | V-RVL-D-200P-TH-N-075 | V-RVL-D-200P-TL-N-075 | V-RVL-D-200P-SS-N-075 | Duplex, 7.5 Hp | 100 | 7.5 | 15270 | 49.3 | 22.8/11.0 | 73 | 57 x 50 x 82 | 72 x 48 x 63 | 86 x 40 x 66 | 62 x 52 x 86 | 7 | 3.9/2.25 | 50 | V-RVD-D-200P-SS-N-100 | V-RVD-D-200P-SS-N-100 |  |  | Duplex, 10 Hp | 100 | 10 | 22910 | 55.2 | 29.4/15.3 | 78 | 62 x 52 x 86 | 86 x 47 x 66 |  |  | 100 | 10 | 10 | 10 | 10 | 3.5 | 1.2 | 0.5 | 0.14
| Locations | 2/Room |  | 1 |  | 50 | 0 | 0 | [8 empty] | 3000 | 1.2318 | 27 |  |  |  |  | 34 | 58 | 60 | V-RVL-D-200P-TS-N-100 | V-RVL-D-200P-TH-N-100 | V-RVL-D-200P-TL-N-100 | V-RVL-D-200P-SS-N-100 | Duplex, 10 Hp | 100 | 10 | 20360 | 73.1 | 28.0/13.0 | 76 | 57 x 50 x 82 | 72 x 48 x 63 | 86 x 40 x 66 | 62 x 52 x 86 | 4 | 64 | 100 | V-RVD-T-200P-SS-N-100 |  |  |  | Triplex, 10 Hp | 200 | 10 | 22910 | 110.4 | 29.4/15.3 | 81 | 62 x 52 x 96 |  |  |  | 110 | 10 | 10 | 10 | 10 | 10 | 1.4 | 0.6 | 0.165 |  |  |  | pipe dia:
7 | Evacuation Vacuum | 2/Room |  | 1 |  | 100 | 0 | 0 | [8 empty] | 3500 | 1.2896 | 26.5 |  |  |  |  | 26 | 34 x 38 x 68 | 70 | V-RVL-T-200P-SS-N-075 |  |  |  | Triplex, 7.5 Hp | 150 | 7.5 | 15270 | 98.6 | 22.8/11.0 | 76 | 62 x 52 x 86 |  |  |  | 2 | 32 x 38 x 67 | 165 | V-RVD-Q-200P-SS-N-100 |  |  |  | Quad, 10 Hp | 400 | 10 | 22910 | 165.6 | 29.4/15.3 | 83 | 94 x 62 x 86 |  |  |  | 120 | 10 | 10 | 10 | 10 | 10 | 1.6 | 0.7 | 0.19
[17 empty] | 4000 | 1.3417 | 26.1 |  |  |  |  | 19 | 5.1 | 140 | V-RVL-T-200P-SS-N-100 |  |  |  | Triplex, 10 Hp | 200 | 10 | 20360 | 146.2 | 28.0/13.0 | 79 | 62 x 52 x 86 |  |  |  |  | 3 | [16 empty] | 130 | 10 | 10 | 10 | 10 | 10 | 1.85 | 0.8 | 0.215
Acute Care Locations
[17 empty] | 5000 | 1.4657 | 25.3 |  |  |  |  | 12 | http://amico.com/Air&Vac/Acrobat%20Files/1CAT2002%20-LUB/1DRR5HT120V.pdf | 219 | V-RVL-Q-200P-SS-N-100 |  |  |  | Quad, 10 Hp | 300 | 10 | 20360 | 219.3 | 28.0/13.0 | 81 | 100 x 52 x 86 |  |  |  |  | http://amico.com/Air&Vac/Acrobat%20Files/1CAT2002%20OIL-LESS/1DOB2T120V.pdf | [16 empty] | 140 | 10 | 10 | 10 | 10 | 10 | 2.1 | 0.9 | 0.24
| (Non-Anesthetizing) | [15 empty] | 6000 | 1.6734 | 24.3 |  |  |  |  | 9 | V-RVL-D-080P-TS-N-010 | 280 | V-RVL-T-200P-SS-N-250 |  |  |  | Triplex, 25 Hp | 400 | 25 | 50900 | 350.4 | 69/34.5 | 83 | 132 x 75 x 86 |  |  |  |  | V-RVD-D-080P-TH-N-010 | [16 empty] | 150 | 10 | 10 | 10 | 10 | 10 | 2.3 | 1 | 0.27
1 | Recovery Room | 3/Bed | 1.5 |  |  | 50 | 0 | 0 | [8 empty] | 7000 | 1.941 | 23.4 |  |  |  |  | 5 | 0 | 330 | V-RVL-Q-200P-SS-N-200 |  |  |  | Quad, 20 Hp | 500 | 20 | 40720 | 416.1 | 54/27 | 82 | 132 x 75 x 86 |  |  |  |  | 0 | [16 empty] | 160 | 10 | 10 | 10 | 10 | 10 | 2.6 | 1.1 | 0.3
2 | I.C.U. (Except Cardiac) | 3/Bed | 2 |  |  | 75 | 0 | 0 | [8 empty] | 8000 | 2.1898 | 22.8 |  |  |  |  | 3 | 0 | 525 | V-RVLQ-200P-SS-N-250 |  |  |  | Quad, 25 Hp | 500 | 25 | 50900 | 525.6 | 69/34.5 | 85 | 132 x 75 x 86 |  |  |  |  | 0 | [16 empty] | 170 | 10 | 10 | 10 | 10 | 10 | 2.9 | 1.25 | 0.34
3 | Cardiac I.C.U. | 2/Bed | 1 |  |  | 50 | 0 | 0 | [8 empty] | 9000 | 2.7562 | 21.9 | [5 empty] | 63 x 30 x 40 | [17 empty] | 66 x 34 x 45 | [16 empty] | 180 | 10 | 10 | 10 | 10 | 10 | 3.2 | 1.35 | 0.37 |  |  |  |  | zone 1: riser 1; zone 2: riser 2
4 | Emergency Room | 2/Bed | 1 |  |  | 100 | 0 | 0 | [8 empty] | 10000 | 3.8322 | 21 | [5 empty] | 0 | [17 empty] | 0 | [16 empty] | 190 | 10 | 10 | 10 | 10 | 10 | 3.5 | 1.5 | 0.4 |  |  |  | CFM: | zone 1: 0; zone 2: 0
5 | Special Procedures | [15 empty] | 11000 | 5.3182 | 20.4 | [5 empty] | 0 | [17 empty] | 0 | [16 empty] | 200 | 10 | 10 | 10 | 10 | 10 | 3.8 | 1.65 | 0.44 |  |  |  | length (ft): | zone 1: 0; zone 2: 0
| (X-Ray, dialysis, etc.) | 2/Room |  | 1.5 |  | 30 | 0 | 0 | [16 empty] | http://amico.com/Air&Vac/Acrobat%20Files/1CAT2002%20-LUB/1DRR5HT120.pdf | [17 empty] | http://amico.com/Air&Vac/Acrobat%20Files/1CAT2002%20OIL-LESS/1DOB2T120.pdf | [16 empty] | 220 | 10 | 10 | 10 | 10 | 10 | 10 | 1.95 | 0.53
6 | Catherterization Lab | 2/Room |  | 1 |  | 10 | 0 | 0 | [10 empty] | Exhaust Pipe Sizing | [5 empty] | 0 | 3 | http://amico.com/Air&Vac/Acrobat%20Files/1CAT2002%20-LUB/1DRR5HT120V.pdf | http://amico.com/Air&Vac/Acrobat%20Files/1CAT2002%20-LUB/1DRR5HT120.pdf |  |  | http://www.amico.com/Air&Vac/ss1drrtv.htm | http://www.amico.com/Air&Vac/ss1drrt.htm | [10 empty] | 0 | [28 empty] | pipe dia:
7 | Surgical Excision Room | 1/Room |  | 1 |  | 10 | 0 | 0 | [5 empty] | Total Vacuum Plant | [10 empty] | 0 | 5 | http://amico.com/Air&Vac/Acrobat%20Files/1CAT2002%20-LUB/1DRR5HT120V.pdf | http://amico.com/Air&Vac/Acrobat%20Files/1CAT2002%20-LUB/1DRR5HT120.pdf |  |  | http://www.amico.com/Air&Vac/ss1drrtv.htm | http://www.amico.com/Air&Vac/ss1drrt.htm | [10 empty] | 0
8 | Neonatal I.C.U. | 2/Bed | 1 |  |  | 50 | 0 | 0 | [5 empty] | Capacity (inc. backup) |  |  |  |  | Pipe Length + 30% |  |  |  |  | 0 |  | 9 | http://amico.com/Air&Vac/Acrobat%20Files/1CAT2002%20-LUB/1DRR5HT120V.pdf | http://amico.com/Air&Vac/Acrobat%20Files/1CAT2002%20-LUB/1DRR5HT120.pdf |  |  | http://www.amico.com/Air&Vac/ss1drrtv.htm | http://www.amico.com/Air&Vac/ss1drrt.htm | [11 empty] | 2 | http://amico.com/Air&Vac/Acrobat%20Files/1CAT2002%20OIL-LESS/1DOB2T120V.pdf | http://amico.com/Air&Vac/Acrobat%20Files/1CAT2002%20OIL-LESS/1DOB2T120.pdf |  |  | http://www.amico.com/Air&Vac/ss1dortv.htm | http://www.amico.com/Air&Vac/ss1dort.htm | [9 empty] | SCFM | 3/4" | 1" | 1 1/4" | 1 1/2" | 2" | 2 1/2" | 3" | 4" | 6" | 8" |  |  | zone 1: zones | branches |  |  | risers
[15 empty] | in SCFM: | 1 | 50 | 100 | 150 | 200 | 300 | 400 | 500 | 3 | #N/A | 12 | http://amico.com/Air&Vac/Acrobat%20Files/1CAT2002%20-LUB/1DRR5HT120V.pdf | http://amico.com/Air&Vac/Acrobat%20Files/1CAT2002%20-LUB/1DRR5HT120.pdf |  |  | http://www.amico.com/Air&Vac/ss1drrtv.htm | http://www.amico.com/Air&Vac/ss1drrt.htm | [11 empty] | 4 | http://amico.com/Air&Vac/Acrobat%20Files/1CAT2002%20OIL-LESS/1DOB2T120V.pdf | http://amico.com/Air&Vac/Acrobat%20Files/1CAT2002%20OIL-LESS/1DOB2T120.pdf |  |  | http://www.amico.com/Air&Vac/ss1dortv.htm | http://www.amico.com/Air&Vac/ss1dort.htm | [9 empty] | 5 | 0.0252 | 0.00616 | 0.00196 | 0.00098 |  |  |  |  | 5 |  | 3/4" |  | 3/4" | 3/4" | 3/4" | 3/4" | 3/4" | 3/4" | 3/4" | 3/4" | 3/4" | 3/4" | 3/4" | 3/4" | 3/4" | 3/4" | 3/4"
Sub-Acute Patient Care
[15 empty] | 10 | 1 1/2" | 2" | 2" | 2" | 2" | 2" | 2" | 2" | #N/A |  | 19 | http://amico.com/Air&Vac/Acrobat%20Files/1CAT2002%20-LUB/1DRR5HT120V.pdf | http://amico.com/Air&Vac/Acrobat%20Files/1CAT2002%20-LUB/1DRR5HT120.pdf |  |  | http://www.amico.com/Air&Vac/ss1drrtv.htm | http://www.amico.com/Air&Vac/ss1drrt.htm | [11 empty] | 7 | http://amico.com/Air&Vac/Acrobat%20Files/1CAT2002%20OIL-LESS/1DOB2T120V.pdf | http://amico.com/Air&Vac/Acrobat%20Files/1CAT2002%20OIL-LESS/1DOB2T120.pdf |  |  | http://www.amico.com/Air&Vac/ss1dortv.htm | http://www.amico.com/Air&Vac/ss1dort.htm | [9 empty] | 10 |  | 0.0196 | 0.00644 | 0.00308 | 0.00084 |  |  |  | 5 |  | 3/4" | [11 empty] | 1" | 1" | 1" | 1" | 1" | bar: zone 1 to zone 10
| (Non-Anesthetizing) | [6 empty] | 0 | [6 empty] | 50 | 2" | 2" | 2 1/2" | 3" | 3" | 3" | 3" | 3" | 0 |  | 26 | http://amico.com/Air&Vac/Acrobat%20Files/1CAT2002%20-LUB/1DRR5HT120V.pdf | http://amico.com/Air&Vac/Acrobat%20Files/1CAT2002%20-LUB/1DRR5HT120.pdf |  |  | http://www.amico.com/Air&Vac/ss1drrtv.htm | http://www.amico.com/Air&Vac/ss1drrt.htm | [11 empty] | 10 | http://amico.com/Air&Vac/Acrobat%20Files/1CAT2002%20OIL-LESS/1DOB7.5T120V.pdf | http://amico.com/Air&Vac/Acrobat%20Files/1CAT2002%20OIL-LESS/1DOB7.5T120.pdf |  |  | http://www.amico.com/Air&Vac/ss1dortv.htm | http://www.amico.com/Air&Vac/ss1dort.htm | [9 empty] | 15 |  | 0.0378 | 0.0126 | 0.00588 | 0.00161 |  |  |  | 5 |  | 3/4" | [11 empty] | 1" | 1" | 1" | 1" | 1" | bar: zone 1 to zone 10
1 | Patient Room - Surgical | 1/Bed | 1.5 |  |  | 15 | 0 | 0 | [6 empty] | 100 | 3" | 3" | 3" | 3" | 4" | 4" | 5" | 5" | 3 | #N/A | 34 | http://amico.com/Air&Vac/Acrobat%20Files/1CAT2002%20-LUB/1DRR10T200V.pdf | http://amico.com/Air&Vac/Acrobat%20Files/1CAT2002%20-LUB/1DRR10T200.pdf | http://amico.com/Air&Vac/Acrobat%20Files/1CAT2002%20-LUB/1DRR10T200N.pdf | http://amico.com/Air&Vac/Acrobat%20Files/1CAT2002%20-LUB/1DRR10S200.pdf | http://www.amico.com/Air&Vac/ss1drrtv.htm | http://www.amico.com/Air&Vac/ss1drrt.htm | http://www.amico.com/Air&Vac/ss1drrt.htm | http://www.amico.com/Air&Vac/ss1drrs.htm | [9 empty] | 16 | http://amico.com/Air&Vac/Acrobat%20Files/1CAT2002%20OIL-LESS/1DOB7.5T120V.pdf | http://amico.com/Air&Vac/Acrobat%20Files/1CAT2002%20OIL-LESS/1DOB7.5T120.pdf |  |  | http://www.amico.com/Air&Vac/ss1dortv.htm | http://www.amico.com/Air&Vac/ss1dort.htm | [9 empty] | 20 |  |  | 0.021 | 0.01015 | 0.00273 | 0.00091 |  |  | 5 |  | 3/4" |  | 1 1/4" | 1 1/4" | 1 1/4" | 1 1/4" | 1 1/4" | 1 1/4" | 1 1/4" | 1 1/4" | 1 1/4" | 1 1/4" | 1 1/4" | 1 1/4" | 1 1/4" | 1 1/4" | 1 1/4"
2 | Patient Room - Medical | 1/Bed |  |  | 1 | 10 | 0 | 0 | [6 empty] | 150 | 3" | 3" | 4" | 4" | 4" | 5" | 5" | 5" | #N/A |  | 60 | http://amico.com/Air&Vac/Acrobat%20Files/1CAT2002%20-LUB/1DRR10T200V.pdf | http://amico.com/Air&Vac/Acrobat%20Files/1CAT2002%20-LUB/1DRR10T200.pdf | http://amico.com/Air&Vac/Acrobat%20Files/1CAT2002%20-LUB/1DRR10T200N.pdf | http://amico.com/Air&Vac/Acrobat%20Files/1CAT2002%20-LUB/1DRR10S200.pdf | http://www.amico.com/Air&Vac/ss1drrtv.htm | http://www.amico.com/Air&Vac/ss1drrt.htm | http://www.amico.com/Air&Vac/ss1drrt.htm | http://www.amico.com/Air&Vac/ss1drrs.htm | [9 empty] | 23 | http://amico.com/Air&Vac/Acrobat%20Files/1CAT2002%20OIL-LESS/1DOB7.5T120V.pdf | http://amico.com/Air&Vac/Acrobat%20Files/1CAT2002%20OIL-LESS/1DOB7.5T120.pdf | http://amico.com/Air&Vac/Acrobat%20Files/1CAT2002%20OIL-LESS/1DOB7.5S120.pdf |  | http://www.amico.com/Air&Vac/ss1dortv.htm | http://www.amico.com/Air&Vac/ss1dort.htm | http://www.amico.com/Air&Vac/ss1dors.htm | [8 empty] | 25 |  |  | 0.0315 | 0.0154 | 0.0042 | 0.0014 |  |  | 5 |  | 3/4" |  | 1 1/4" | 1 1/4" | 1 1/4" | 1 1/4" | 1 1/4" | 1 1/4" | 1 1/4" | 1 1/4" | 1 1/4" | 1 1/4" | 1 1/4" | 1 1/4" | 1 1/4" | 1 1/4" | 1 1/4"
3 | Exam & | 1/Room |  | 1 |  | 10 | 0 | 0 | [6 empty] | 200 | 4" | 4" | 4" | 4" | 5" | 5" | 5" | 5" |  |  | 70 | http://amico.com/Air&Vac/Acrobat%20Files/1CAT2002%20-LUB/1TRR10S200.pdf |  |  |  | http://www.amico.com/Air&Vac/ss1trrs.htm | [12 empty] | 50 | http://amico.com/Air&Vac/Acrobat%20Files/1CAT2002%20OIL-LESS/1DOB10S200.pdf | http://amico.com/Air&Vac/Acrobat%20Files/1CAT2002%20OIL-LESS/1DOB10T200.pdf |  |  | http://www.amico.com/Air&Vac/ss1dors.htm | http://www.amico.com/Air&Vac/ss1dort.htm | [9 empty] | 30 |  |  | 0.0441 | 0.0217 | 0.00574 | 0.00196 | 0.00084 |  | 5 |  | 3/4" |  | 1 1/4" | 1 1/2" | 2" | 2 1/2" | 3" | 4" | 6" | 8" | 0 | 0 | 1 1/4" | 1 1/2" | 2" | 1 1/4" | 1 1/2"
Treatment Room
4 | Nursery | 1/4Bassinets |  |  | 1 | 10 | 0 | 0 | [6 empty] | 300 | 4" | 4" | 5" | 5" | 5" | 6" | 6" | 6" |  |  | 140 | http://amico.com/Air&Vac/Acrobat%20Files/1CAT2002%20-LUB/1TRR10S200.pdf |  |  |  | http://www.amico.com/Air&Vac/ss1trrs.htm | [12 empty] | 100 | http://amico.com/Air&Vac/Acrobat%20Files/1CAT2002%20OIL-LESS/1TOR10S200.pdf |  |  |  | http://www.amico.com/Air&Vac/ss1tors.htm | [10 empty] | 35 |  |  |  | 0.028 | 0.00756 | 0.00252 | 0.001085 |  | 5 |  | 3/4" |  | 1 1/2" | 1 1/2" | 1 1/2" | 1 1/2" | 1 1/2" | 1 1/2" | 1 1/2" | 1 1/2" | 1 1/2" | 1 1/2" | 1 1/2" | 1 1/2" | 1 1/2" | 1 1/2" | 1 1/2"
5 | Nursery Premature | 1/Bassinet | 1 |  |  | 25 | 0 | 0 | [6 empty] | 400 | 5" | 5" | 5" | 6" | 6" | 6" | 8" | 8" |  |  | 219 | http://amico.com/Air&Vac/Acrobat%20Files/1CAT2002%20-LUB/1QRR10S200.pdf |  |  |  | http://www.amico.com/Air&Vac/ss1qrrs.htm | [12 empty] | 165 | http://amico.com/Air&Vac/Acrobat%20Files/1CAT2002%20OIL-LESS/1QOR10S200.pdf |  |  |  | http://www.amico.com/Air&Vac/ss1qors.htm | [10 empty] | 40 |  |  |  | 0.035 | 0.00945 | 0.00322 | 0.001365 |  | 5 |  | 3/4" |  | 1 1/2" | 1 1/2" | 1 1/2" | 1 1/2" | 1 1/2" | 1 1/2" | 1 1/2" | 1 1/2" | 1 1/2" | 1 1/2" | 1 1/2" | 1 1/2" | 1 1/2" | 1 1/2" | 1 1/2"
[15 empty] | 500 | 5" | 5" | 6" | 6" | 6" | 8" | 8" | 8" |  |  | 280 | http://amico.com/Air&Vac/Acrobat%20Files/1CAT2002%20-LUB/1TRR25S200.pdf |  |  |  | http://www.amico.com/Air&Vac/ss1trrs.htm | [11 empty] | http://www.amico.com/Air&Vac/ss1dortv.htm | [16 empty] | 45 |  |  |  | 0.042 | 0.01155 | 0.00392 | 0.00168 |  | 5 |  | 3/4" |  | 1 1/2" | 1 1/2" | 1 1/2" | 1 1/2" | 1 1/2" | 1 1/2" | 1 1/2" | 1 1/2" | 1 1/2" | 1 1/2" | 1 1/2" | 1 1/2" | 1 1/2" | 1 1/2" | 1 1/2"
Other Patient Rooms
[26 empty] | 330 | http://amico.com/Air&Vac/Acrobat%20Files/1CAT2002%20-LUB/1QRR25S200.pdf |  |  |  | http://www.amico.com/Air&Vac/ss1qrrs.htm | [11 empty] | http://www.amico.com/Air&Vac/ss1dort.htm | [16 empty] | 50 |  |  |  | 0.0504 | 0.01365 | 0.00462 | 0.00196 |  | 5 |  | 3/4" |  | 1 1/2" | 1 1/2" | 1 1/2" | 1 1/2" | 1 1/2" | 1 1/2" | 1 1/2" | 1 1/2" | 1 1/2" | 1 1/2" | 1 1/2" | 1 1/2" | 1 1/2" | 1 1/2" | 1 1/2"
1 | Respiratory Care Dep't | 1/Room |  |  | 1.5 | 10 | 0 | 0 | [17 empty] | 525 | http://amico.com/Air&Vac/Acrobat%20Files/1CAT2002%20-LUB/1QRR25S200.pdf |  |  |  | http://www.amico.com/Air&Vac/ss1qrrs.htm | [11 empty] | 0 | [16 empty] | 60 |  |  |  |  | 0.0189 | 0.0063 | 0.00273 | 0.000735 | [14 empty] | 2" | 2" | 2" | 2" | 2" | bar: zone 1 to zone 10
2 | Central Supply, Equip't | [23 empty] | http://www.amico.com/Air&Vac/ss1drrtv.htm | [17 empty] | 0 | [16 empty] | 70 |  |  |  |  | 0.0252 | 0.0084 | 0.00364 | 0.00098 | 5 |  | 3/4" | [11 empty] | 2" | 2" | 2" | 2" | 2" | bar: zone 1 to zone 10
3 | Repair/Calibration, | [23 empty] | http://www.amico.com/Air&Vac/ss1drrt.htm | [34 empty] | 80 |  |  |  |  | 0.0322 | 0.01085 | 0.00476 | 0.00126 | 5 |  | 3/4" | [11 empty] | 2" | 2" | 2" | 2" | 2" | bar: zone 1 to zone 10
4 | Teaching | 1/Room |  |  | 1.5 | 10 | 0 | 0 | [16 empty] | 0 | [34 empty] | 90 |  |  |  |  | 0.0406 | 0.01365 | 0.00588 | 0.00161 | 5 |  | 3/4" | [11 empty] | 2" | 2" | 2" | 2" | 2" | bar: zone 1 to zone 10
5 | Autopsy | 1/Table |  |  | 1.5 | 10 | 0 | 0 | [16 empty] | 0 | [34 empty] | 100 |  |  |  |  | 0.049 | 0.0168 | 0.007 | 0.00196 | [14 empty] | 2" | 2" | 2" | 2" | 2" | bar: zone 1 to zone 10
[60 empty] | 110 | [5 empty] | 0.0196 | 0.0084 | 0.00231 | 5 |  | 3/4" |  | 2 1/2" | 2 1/2" | 2 1/2" | 2 1/2" | 2 1/2" | 2 1/2" | 2 1/2" | 2 1/2" | 2 1/2" | 2 1/2" | 2 1/2" | 2 1/2" | 2 1/2" | 2 1/2" | 2 1/2"
Future Expansion | [7 empty] | 0 | [51 empty] | 120 | [5 empty] | 0.0224 | 0.0098 | 0.00266 | 5 |  | 3/4" |  | 2 1/2" | 2 1/2" | 2 1/2" | 2 1/2" | 2 1/2" | 2 1/2" | 2 1/2" | 2 1/2" | 2 1/2" | 2 1/2" | 2 1/2" | 2 1/2" | 2 1/2" | 2 1/2" | 2 1/2"
[60 empty] | 130 |  | this chart = del P above x 1.4/100 |  |  |  | 0.0259 | 0.0112 | 0.00301 |  |  |  |  | 2 1/2" | 2 1/2" | 2 1/2" | 2 1/2" | 2 1/2" | 2 1/2" | 2 1/2" | 2 1/2" | 2 1/2" | 2 1/2" | 2 1/2" | 2 1/2" | 2 1/2" | 2 1/2" | 2 1/2"
[5 empty] | PEAK CALCULATED DEMAND IN SCFM: |  |  | 0 | [51 empty] | 140 | [5 empty] | 0.0294 | 0.0126 | 0.00336 |  |  |  |  | 2 1/2" | 2 1/2" | 2 1/2" | 2 1/2" | 2 1/2" | 2 1/2" | 2 1/2" | 2 1/2" | 2 1/2" | 2 1/2" | 2 1/2" | 2 1/2" | 2 1/2" | 2 1/2" | 2 1/2"
[60 empty] | 150 | [5 empty] | 0.0322 | 0.014 | 0.00378 |  |  |  |  | 2 1/2" | 2 1/2" | 2 1/2" | 2 1/2" | 2 1/2" | 2 1/2" | 2 1/2" | 2 1/2" | 2 1/2" | 2 1/2" | 2 1/2" | 2 1/2" | 2 1/2" | 2 1/2" | 2 1/2"
[7 empty] | Altitude above sea level, ft: | 0 | [51 empty] | 160 | [5 empty] | 0.0364 | 0.0154 | 0.0042 |  |  |  |  | 2 1/2" | 2 1/2" | 2 1/2" | 2 1/2" | 2 1/2" | 2 1/2" | 2 1/2" | 2 1/2" | 2 1/2" | 2 1/2" | 2 1/2" | 2 1/2" | 2 1/2" | 2 1/2" | 2 1/2"
[60 empty] | 170 | [5 empty] | 0.0406 | 0.0175 | 0.00476 |  |  |  |  | 2 1/2" | 2 1/2" | 2 1/2" | 2 1/2" | 2 1/2" | 2 1/2" | 2 1/2" | 2 1/2" | 2 1/2" | 2 1/2" | 2 1/2" | 2 1/2" | 2 1/2" | 2 1/2" | 2 1/2"
|  |  | PEAK CALCULATED DEMAND IN SCFM, ALTITUDE ADJUSTED: |  |  |  |  | 0 | [51 empty] | 180 | [5 empty] | 0.0448 | 0.0189 | 0.00518 |  |  |  |  | 2 1/2" | 2 1/2" | 2 1/2" | 2 1/2" | 2 1/2" | 2 1/2" | 2 1/2" | 2 1/2" | 2 1/2" | 2 1/2" | 2 1/2" | 2 1/2" | 2 1/2" | 2 1/2" | 2 1/2"
[60 empty] | 190 | [5 empty] | 0.049 | 0.021 | 0.0056 |  |  |  |  | 2 1/2" | 2 1/2" | 2 1/2" | 2 1/2" | 2 1/2" | 2 1/2" | 2 1/2" | 2 1/2" | 2 1/2" | 2 1/2" | 2 1/2" | 2 1/2" | 2 1/2" | 2 1/2" | 2 1/2"
[6 empty] | System |  | Amps | Total | [50 empty] | 200 | [5 empty] | 0.0532 | 0.0231 | 0.00616 |  |  |  |  | 2 1/2" | 2 1/2" | 2 1/2" | 2 1/2" | 2 1/2" | 2 1/2" | 2 1/2" | 2 1/2" | 2 1/2" | 2 1/2" | 2 1/2" | 2 1/2" | 2 1/2" | 2 1/2" | 2 1/2"
|  | System |  | Horsepower |  | Capacity | Btu/h | @ 208/460V | Noise | Dimensions (in) |  | Catalog | Sugg'd | [46 empty] | 220 | [6 empty] | 0.0273 | 0.00742 | [14 empty] | 3" | 3" | 3" | 3" | 3" | bar: zone 1 to zone 10
|  | Model # |  | each | total | SCFM @ 19" Hg | each pump | each pump | level (dB) | L x W x H |  | Cuts: | Specs: | [46 empty] | 530 | [8 empty] | 0.01 | 0.007 | [15 empty] | 6" | 6"
Recommended
| System: | [58 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28
Alternate 1:
| Alternate 2: | [58 empty] | 1: 530
220
| Alternate 3: | [58 empty] | 1: 200
190
| The pump models specified are sized according to the calculated demand in SCFM adjusted to the indicated altitude. | [58 empty] | 1: 180
| The Btu/hr and amperage listed are for each pump. | [58 empty] | 1: 170
| The noise level indicated is for the complete system. | [58 empty] | 1: 160
150
|  |  | EXHAUST LINE SIZING | [56 empty] | 1: 140
|  |  |  | Length, Ft: | [55 empty] | 1: 130
|  |  |  | Line Dia: | [55 empty] | 1: 120
110
| Lubricated rotary vane systems are generally more reliable than dry systems and could be used for combination surgical/anesthesia applications. | [58 empty] | 1: 100
| However, if this system is dedicated for waste anesthesia removal only, then utilize the dry vane system below: | [58 empty] | 1: 90
80
[6 empty] | System |  | Amps | Total | [50 empty] | 1: 70
|  | System |  | Horsepower |  | Capacity | Btu/h | @ 208/460V | Noise | Dimensions (in) |  | Catalog | Sugg'd | [46 empty] | 1: 60
|  | Model # |  | each | total | SCFM @ 19" Hg | each pump | each pump | level (dB) | L x W x H |  | Cuts: | Specs: | [46 empty] | 1: 50
| Recommended | [58 empty] | 1: 45
| System: | [58 empty] | 1: 40
| Alternate 1: | [58 empty] | 1: 35
30
| Alternate 2: | [58 empty] | 1: 25
20
| Alternate 3: | [58 empty] | 1: 15
10
5
EXHAUST LINE SIZING
Length, Ft:
Line Dia:
For all length input, enter the actual, measured run of pipe. The equivalent length of pipe (due to additional friction loss
through fittings, filters, valves, etc.) is automatically calculated and used to determine the proper pipe diameter.
ZONE PIPE SIZING
|  | Zone #1 | Zone #2 | Zone #3 | Zone #4 | Zone #5 | Zone #6 | Zone #7 | Zone #8 | Zone #9 | Zone #10
Flow SCFM:
Length, Ft:
Zone Dia.
For all length input, enter the actual, measured run of pipe. The equivalent length of pipe (due to additional friction loss
through fittings, filters, valves, etc.) is automatically calculated and used to determine the proper pipe diameter.
BRANCH PIPE SIZING
[5 empty] | Branch #1 | Branch #2 | Branch #3
Flow SCFM:
Length, Ft:
Branch Dia.
For all length input, enter the actual, measured run of pipe. The equivalent length of pipe (due to additional friction loss
through fittings, filters, valves, etc.) is automatically calculated and used to determine the proper pipe diameter.
RISER PIPE SIZING
[5 empty] | Riser #1: | Riser #2:
Flow SCFM:
Length, Ft:
Riser Dia.

## medical air
Name of Facility: | [49 empty] | AIR
pressure drop in psi per 100 ft of pipe
Project Number:
[50 empty] | CFM | 1/2" | 3/4" | 1" | 1 1/4" | 1 1/2" | 2" | 2 1/2"
ENTER REQUIRED DATA IN THE BLUE SHADED AREAS BELOW | [49 empty] | 5 | 0.027813 | 0.02628 | [6 empty] | #N/A | #N/A | #N/A |  | branch 1 | branch 2 | branch 3
[50 empty] | 10 | 0.11103 | 0.17082 | 0.04818 | [5 empty] | #N/A | #N/A | #N/A | CFM: | 0 | 0 | 0
LOCATION OF OUTLETS |  | MEDICAL AIR | [47 empty] | 15 | 0.24966 | 0.38544 | 0.10731 | [5 empty] | #N/A | #N/A | #N/A | length (ft): | 0 | 0 | 0
|  | Free Air Allowance, SCFM |  |  |  | Simultaneous | Number of Units, | Air | [41 empty] | 20 |  | 0.66576 | 0.19053 | 0.0438
|  | Per Unit | Per Bed | Per Room | Per Outlet | use Factor | Beds, Rooms, Outlets | SCFM | [41 empty] | 25 |  | 1.095 | 0.29784 | 0.07008 | [7 empty] | pipe dia:
Anesthetizing Locations | [49 empty] | 30 |  | 1.5418 | 0.42924 | 0.09855
[27 empty] | recommended | recommended | total |  |  |  | amps | noise |  |  |  |  | alternate | alternate | alt - total | alt | alt | alt | alt - amps | alt - noise | alt |  |  | 35 |  | 2.1002 | 0.58254 | 0.13578 | 0.05913 | [7 empty] | #DIV/0! | #DIV/0! | #DIV/0!
1 | Special surgery and |  |  | 0.5 |  | 100 | 0 | 0 | [8 empty] | Altitude Compensation | [8 empty] | scfm | model # | desc | usage | Hp | Btu/h | sys cap | 208/460 | level | dims | cat url | spec url |  | model # | desc | usage | Hp | Btu/h | sys cap | 208/460 | level | dims | cat url | spec url | 40 |  | 2.7441 | 0.76212 | 0.17739 | 0.07884 | [7 empty] | = 2" x 100 ft x 1.2
| cardiovascular | [15 empty] | feet | mult | [5 empty] | 160 | 3.6 | 3.6 | A-RED-D-080P-TH-N-015 | Duplex, 1.5 Hp | 20 | 1.5 | 3817.5 | 5.2 | 4.5/2.1 | 71 | 82 x 30 x 60 | http://www.amico.com/Air&Vac/Acrobat%20Files/3CAT2002/3DOX5PT120D.pdf | http://www.amico.com/Air&Vac/ss3doxptd.htm |  | A-SCD-D-080P-SS-N-020 | Duplex, 2 Hp | 20 | 2 | 4581 | 6.7 | 6.7/3.2 | 59 | 47.5 x 34 x 72 | http://www.amico.com/Air&Vac/Acrobat%20Files/3CAT2002/3DOXS5PS80D.pdf | http://www.amico.com/Air&Vac/ss3doxspsd.htm | 45 |  |  | 0.9636 | 0.22338 | 0.09855 | [7 empty] | length (ft) x 1.4
2 | Major surgery and |  |  | 0.5 |  | 100 | 0 | 0 | [7 empty] | 0 | 0 | 1 | [5 empty] | 125 | A-RED-D-080P-TH-N-015 | 4.5 | A-RED-D-120P-TH-N-020 | Duplex, 2 Hp | 20 | 2 | 5090 | 7.6 | 6.7/3.2 | 71 | 82 x 33 x 60 | http://www.amico.com/Air&Vac/Acrobat%20Files/3CAT2002/3DOX5PT120D.pdf | http://www.amico.com/Air&Vac/ss3doxptd.htm | A-SCD-D-080P-SS-N-020 | A-SCD-D-080P-SS-N-020 | Duplex, 2 Hp | 20 | 2 | 4581 | 6.7 | 6.7/3.2 | 59 | 47.5 x 34 x 72 | http://www.amico.com/Air&Vac/Acrobat%20Files/3CAT2002/3DOXS5PS80D.pdf | http://www.amico.com/Air&Vac/ss3doxspsd.htm | 50 |  |  | 1.1914 | 0.2628 | 0.12264
| orthopedic | [14 empty] | 0 | 1600 | 1.05 | [5 empty] | 90 | Duplex, 1.5 Hp | 5.3 | A-RED-D-120P-TH-N-020 | Duplex, 2 Hp | 20 | 2 | 5090 | 7.6 | 6.7/3.2 | 71 | 82 x 33 x 60 | http://www.amico.com/Air&Vac/Acrobat%20Files/3CAT2002/3DOX5PT120D.pdf | http://www.amico.com/Air&Vac/ss3doxptd.htm | Duplex, 2 Hp | A-SCD-D-080P-SS-N-030 | Duplex, 3 Hp | 20 | 3 | 6871.5 | 9.7 | 10/4.6 | 59 | 47.5 x 34 x 72 | http://www.amico.com/Air&Vac/Acrobat%20Files/3CAT2002/3DOXS5PS80D.pdf | http://www.amico.com/Air&Vac/ss3doxspsd.htm | 60 |  |  | 1.7148 | 0.39858 | 0.1752 | 0.04818
3 | Minor surgery |  |  | 0.5 |  | 75 | 0 | 0 | [8 empty] | 3300 | 1.11 | [5 empty] | 85 | 20 | 7 | A-RED-D-120P-TH-N-030 | Duplex, 3 Hp | 20 | 3 | 6871.5 | 10.1 | 10.8/4.6 | 71 | 82 x 33 x 60 | http://www.amico.com/Air&Vac/Acrobat%20Files/3CAT2002/3DOX5PT120D.pdf | http://www.amico.com/Air&Vac/ss3doxptd.htm | 20 | A-SCD-D-080P-SS-N-030 | Duplex, 3 Hp | 20 | 3 | 6871.5 | 9.7 | 10/4.6 | 59 | 47.5 x 34 x 72 | http://www.amico.com/Air&Vac/Acrobat%20Files/3CAT2002/3DOXS5PS80D.pdf | http://www.amico.com/Air&Vac/ss3doxspsd.htm | 70 |  |  | 2.3345 | 0.54093 | 0.23871 | 0.06351 | [6 empty] | zone 1 | zone 2 | zone 3 | zone 4 | zone 5 | zone 6 | zone 7 | zone 8 | zone 9 | zone 10
4 | Emergency surgery |  |  | 0.5 |  | 25 | 0 | 0 | [8 empty] | 5000 | 1.17 | [5 empty] | 50 | 1.5 | 11.2 | A-RED-D-120P-TH-N-050 | Duplex, 5 Hp | 40 | 5 | 11452.5 | 17.9 | 16.1/7.9 | 75 | 89 x 34 x 66 | http://www.amico.com/Air&Vac/Acrobat%20Files/3CAT2002/3DOX5PT120D.pdf | http://www.amico.com/Air&Vac/ss3doxptd.htm | 2 | A-SCD-D-080P-SS-N-050 | Duplex, 5 Hp | 40 | 5 | 11452.5 | 16.1 | 15.8/7.4 | 59 | 47.5 x 34 x 72 | http://www.amico.com/Air&Vac/Acrobat%20Files/3CAT2002/3DOXS5PS80D.pdf | http://www.amico.com/Air&Vac/ss3doxspsd.htm | 80 |  |  | 3.0485 | 0.71175 | 0.31317 | 0.08322 | [5 empty] | CFM: | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | Radiology |  |  | 0.5 |  | 10 | 0 | 0 | [8 empty] | 6600 | 1.24 | [5 empty] | 45 | 3817.5 | 14.5 | A-RED-D-120P-TH-N-050 | Duplex, 5 Hp | 40 | 5 | 11452.5 | 17.9 | 16.1/7.9 | 75 | 89 x 34 x 66 | http://www.amico.com/Air&Vac/Acrobat%20Files/3CAT2002/3DOX5PT120D.pdf | http://www.amico.com/Air&Vac/ss3doxptd.htm | 4581 | A-SCD-T-120P-SS-N-050 | Triplex, 5 Hp | 40 | 5 | 11452.5 | 32.2 | 15.8/7.4 | 62 | 58 x 49 x 88 | http://www.amico.com/Air&Vac/Acrobat%20Files/3CAT2002/3TOXS5PS120D.pdf | http://www.amico.com/Air&Vac/ss3toxspsd.htm | 90 |  |  |  | 0.89571 | 0.39639 | 0.10512 | [5 empty] | length (ft): | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | Cardiac catheterization |  |  | 0.5 |  | 10 | 0 | 0 | [8 empty] | 8200 | 1.31 | [5 empty] | 40 | 4.5/2.1 | 19.2 | A-RED-D-120P-SS-N-075 | Duplex, 7.5 Hp | 40 | 7.5 | 17178.75 | 27.6 | 25.1/12.4 | 76 | 82 x 60 x 84 | http://www.amico.com/Air&Vac/Acrobat%20Files/3CAT2002/3DOX15PS120D.pdf | http://www.amico.com/Air&Vac/ss3doxpsd.htm | 6.7/3.2 | A-SCD-T-120P-SS-N-050 | Triplex, 5 Hp | 40 | 5 | 11452.5 | 32.2 | 15.8/7.4 | 62 | 58 x 49 x 88 | http://www.amico.com/Air&Vac/Acrobat%20Files/3CAT2002/3TOXS5PS120D.pdf | http://www.amico.com/Air&Vac/ss3toxspsd.htm | 100 |  |  |  | 1.1069 | 0.48837 | 0.1314 | 0.050678
7 | Ventilators | 3.5 |  |  |  | 100 | 0 | 0 | [8 empty] | 9900 | 1.39 | [5 empty] | 27 | 71 | 22 | A-RED-D-120P-SS-N-100 | Duplex, 10 Hp | 110 | 10 | 22905 | 35 | 34.3/15.5 | 76 | 82 x 60 x 84 | http://www.amico.com/Air&Vac/Acrobat%20Files/3CAT2002/3DOX15PS120D.pdf | http://www.amico.com/Air&Vac/ss3doxpsd.htm | 59 | A-SCD-T-120P-SS-N-050 | Triplex, 5 Hp | 40 | 5 | 11452.5 | 32.2 | 15.8/7.4 | 62 | 58 x 49 x 88 | http://www.amico.com/Air&Vac/Acrobat%20Files/3CAT2002/3TOXS5PS120D.pdf | http://www.amico.com/Air&Vac/ss3toxspsd.htm | 110 |  |  |  | 1.3381 | 0.5913 | 0.15768 | 0.06132 |  |  |  |  | pipe dia:
8 | Delivery rooms |  |  | 0.5 |  | 100 | 0 | 0 | [15 empty] | 22 | 82 x 30 x 60 | 27 | A-RED-D-120P-SS-N-100 | Duplex, 10 Hp | 110 | 10 | 22905 | 35 | 34.3/15.5 | 76 | 82 x 60 x 84 | http://www.amico.com/Air&Vac/Acrobat%20Files/3CAT2002/3DOX15PS120D.pdf | http://www.amico.com/Air&Vac/ss3doxpsd.htm | 47.5 x 34 x 72 | A-SCD-Q-120P-SS-N-050 | Quad, 5 Hp | 40 | 5 | 11452.5 | 48.3 | 15.8/7.4 | 64 | 72 x 44 x 88 | http://www.amico.com/Air&Vac/Acrobat%20Files/3CAT2002/3QOXS5PS120D.pdf | http://www.amico.com/Air&Vac/ss3qoxspsd.htm | 120 |  |  |  | 1.5921 | 0.70518 | 0.18834 | 0.07227
[24 empty] | 19.2 | 5.2 | 40 | A-RED-D-120P-SS-N-150 | Duplex, 15 Hp | 110 | 15 | 34357.5 | 53.5 | 46.6/23.3 | 79 | 82 x 60 x 84 | http://www.amico.com/Air&Vac/Acrobat%20Files/3CAT2002/3DOX15PS120D.pdf | http://www.amico.com/Air&Vac/ss3doxpsd.htm | 6.7 | A-SCD-Q-120P-SS-N-050 | Quad, 5 Hp | 40 | 5 | 11452.5 | 48.3 | 15.8/7.4 | 64 | 72 x 44 x 88 | http://www.amico.com/Air&Vac/Acrobat%20Files/3CAT2002/3QOXS5PS120D.pdf | http://www.amico.com/Air&Vac/ss3qoxspsd.htm | 130 |  |  |  | 1.8681 | 0.82782 | 0.22119 | 0.08541
Acute Care Locations
[24 empty] | 14.5 | http://www.amico.com/Air&Vac/Acrobat%20Files/3CAT2002/3DOX5PT120D.pdf | 45 | A-RED-D-120P-SS-N-150 | Duplex, 15 Hp | 110 | 15 | 34357.5 | 53.5 | 46.6/23.3 | 79 | 82 x 60 x 84 | http://www.amico.com/Air&Vac/Acrobat%20Files/3CAT2002/3DOX15PS120D.pdf | http://www.amico.com/Air&Vac/ss3doxpsd.htm | [12 empty] | 140 |  |  |  | 2.1659 | 0.95922 | 0.25623 | 0.10074
| (Non-Anesthetizing) | [22 empty] | 11.2 | http://www.amico.com/Air&Vac/ss3doxptd.htm | 50 | A-RED-T-200P-SS-N-075 | Triplex, 7.5 Hp | 110 | 7.5 | 17178.75 | 55.2 | 25.1/12.4 | 79 | 80 x 60 x 88 | http://www.amico.com/Air&Vac/Acrobat%20Files/3CAT2002/3TOX15PS200D.pdf | http://www.amico.com/Air&Vac/ss3toxpsd.htm | [12 empty] | 150 |  |  |  | 2.4878 | 1.1016 | 0.29346 | 0.11388
1 | Recovery room/surgical |  | 2 |  |  | 25 | 0 | 0 | [15 empty] | 7 | http://www.amico.com/Air&Vac/Acrobat%20Files/3CAT2002/3DOXS5PS80D.pdf | 85 | A-RED-T-200P-SS-N-150 | Triplex, 15 Hp | 160 | 15 | 34357.5 | 107 | 46.6/23.3 | 82 | 80 x 60 x 88 | http://www.amico.com/Air&Vac/Acrobat%20Files/3CAT2002/3TOX15PS200D.pdf | http://www.amico.com/Air&Vac/ss3toxpsd.htm | [12 empty] | 160 |  |  |  | 2.847 | 1.2527 | 0.33288 | 0.12973
| (postanesthesia) | [22 empty] | 5.3 | http://www.amico.com/Air&Vac/ss3doxspsd.htm | 90 | A-RED-T-240P-SS-N-200 | Triplex, 20 Hp | 200 | 20 | 45810 | 130.2 | 63.7/28.8 | 84 | 118 x 70 x 94 | http://www.amico.com/Air&Vac/Acrobat%20Files/3CAT2002/3TOQ20MS240D.pdf | http://www.amico.com/Air&Vac/ss3toqpsd.htm | [12 empty] | 170 |  |  |  | 3.2149 | 1.4191 | 0.29346 | 0.14646
2 | ICU/CCU |  | 2 |  |  | 50 | 0 | 0 | [15 empty] | 4.5 |  | 125 | A-REN-Q-200P-SS-N-150 | Quad, 15 Hp | 260 | 15 | 34357.5 | 160.5 | 46.6/23.3 | 84 | 80 x 60 x 88 | [14 empty] | 180 |  |  |  | 3.5828 | 1.5856 | 0.42048 | 0.1642 | [5 empty] | zone 1: riser 1; zone 2: riser 2
3 | Emergency Room |  | 2 |  |  | 10 | 0 | 0 | [15 empty] | 3.6 |  | 160 | A-REN-Q-200P-SS-N-200 | Quad, 20 Hp | 260 | 20 | 45810 | 195.3 | 63.7/28.8 | 86 | 118 x 70 x 94 | [14 empty] | 190 |  |  |  | 4.0052 | 1.7695 | 0.37668 | 0.18295 |  |  |  |  | CFM: | zone 1: 0; zone 2: 0
4 | Neonatal ICU |  | 1.5 |  |  | 75 | 0 | 0 | [17 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 200 |  |  |  | 4.4276 | 1.9535 | 0.5256 | 0.20271 |  |  |  |  | length (ft): | 0 | 0
5 | Dialysis units |  | 0.5 |  |  | 10 | 0 | 0
6 | Recovery rooms/OB |  |  | 2 |  | 25 | 0 | 0 | [10 empty] | Intake Pipe Sizing | [42 empty] | pipe dia:
7 | Ventilators | 6 |  |  |  | 100 | 0 | 0 | [6 empty] | Total Air Plant
[15 empty] | Capacity (inc. backup) |  |  |  |  | Pipe Length + 30% |  |  |  |  | 0 | [24 empty] | SCFM | 1/2" | 3/4" | 1" | 1 1/4" | 1 1/2" | 2" | 2 1/2" |  | 6" | 8" |  |  | zones | [9 empty] | branches |  |  | risers
Sub-Acute Patient Care
[16 empty] | in SCFM: | 1 | 50 | 100 | 150 | 200 | 300 | 400 | 500 | 2 | 160 1: #N/A | 5 | 0.00038938 | 0.00036792 | [6 empty] | 5 |  | 1/2" |  | 1/2" | 1/2" | 1/2" | 1/2" | 1/2" | 1/2" | 1/2" | 1/2" | 1/2" | 1/2" | 1/2" | 1/2" | 1/2" | 1/2" | 1/2"
| (Non-Anesthetizing) | [14 empty] | 20 | 1 1/4" | 1 1/4" | 1 1/4" | 1 1/4" | 1 1/4" | 1 1/4" | 1 1/2" | 1 1/2" | #N/A | [24 empty] | 10 | 0.0015545 | 0.0023915 | 0.00067452 |  | this chart = del P above x 1.4/100 |  |  |  | 5 |  | 1/2" |  | 1/2" | 1/2" | 1/2" | 1/2" | 1/2" | 1/2" | 1/2" | 1/2" | 1/2" | 1/2" | 1/2" | 1/2" | 1/2" | 1/2" | 1/2"
1 | Nursery |  | 0.5 |  |  | 25 | 0 | 0 | [7 empty] | 40 | 1 1/2" | 2" | 2" | 2" | 2 1/2" | 2 1/2" | 2 1/2" | 3" | [25 empty] | 15 | 0.0034952 | 0.0053962 | 0.0015023 | [5 empty] | 5 |  | 1/2" |  | 1/2" | 1/2" | 1/2" | 1/2" | 1/2" | 1/2" | 1/2" | 1/2" | 1/2" | 1/2" | 1/2" | 1/2" | 1/2" | 1/2" | 1/2"
2 | Patient rooms |  | 0.5 |  |  | 10 | 0 | 0 | [7 empty] | 110 | 2" | 2 1/2" | 3" | 3" | 4" | 4" | 4" | 4" | [25 empty] | 20 |  | 0.0093206 | 0.0026674 | 0.0006132 |  |  |  |  | 5 |  | 1/2" |  | 3/4" | 3/4" | 3/4" | 3/4" | 3/4" | 3/4" | 3/4" | 3/4" | 3/4" | 3/4" | 3/4" | 3/4" | 3/4" | 3/4" | 3/4"
(where shown)
3 | Exam and Treatment |  |  | 1 |  | 10 | 0 | 0 | [7 empty] | 130 | 3" | 3" | 3" | 3" | 3" | 4" | 4" | 4" | [25 empty] | 25 |  | 0.01533 | 0.0041698 | 0.00098112 |  |  |  |  | 5 |  | 1/2" |  | 3/4" | 3/4" | 3/4" | 3/4" | 3/4" | 3/4" | 3/4" | 3/4" | 3/4" | 3/4" | 3/4" | 3/4" | 3/4" | 3/4" | 3/4"
Room
4 | Preop holding |  |  |  | 1.5 | 20 | 0 | 0 | [7 empty] | 160 | 3" | 3" | 3" | 4" | 4" | 4" | 4" | 4" | [25 empty] | 30 |  | 0.021585 | 0.0060094 | 0.0013797 |  |  |  |  | 5 |  | 1/2" |  | 3/4" | 3/4" | 3/4" | 3/4" | 3/4" | 3/4" | 3/4" | 3/4" | 3/4" | 3/4" | 3/4" | 3/4" | 3/4" | 3/4" | 3/4"
5 | Respiratory care |  |  | 1 |  | 50 | 0 | 0 | [7 empty] | 200 | 4" | 4" | 4" | 4" | 4" | 6" | 6" | 6" | [25 empty] | 35 |  | 0.029403 | 0.0081556 | 0.0019009 | 0.00082782 |  |  |  | 5 |  | 1/2" |  | 3/4" | 3/4" | 3/4" | 3/4" | 3/4" | 3/4" | 3/4" | 3/4" | 3/4" | 3/4" | 3/4" | 3/4" | 3/4" | 3/4" | 3/4"
6 | Pulmonary function lab |  |  |  | 1 | 50 | 0 | 0 | [7 empty] | 260 | 4" | 4" | 4" | 4" | 4" | 6" | 6" | 6" | [25 empty] | 40 |  | 0.038417 | 0.01067 | 0.0024835 | 0.0011038 |  |  |  | 5 |  | 1/2" |  | 3/4" | 3/4" | 3/4" | 3/4" | 3/4" | 3/4" | 3/4" | 3/4" | 3/4" | 3/4" | 3/4" | 3/4" | 3/4" | 3/4" | 3/4"
7 | EEG and EKG |  |  |  | 1 | 50 | 0 | 0 | [7 empty] | 450 | 6" | 6" | 6" | 6" | 8" | 8" | 8" | 8" | [25 empty] | 45 |  |  | 0.01349 | 0.0031273 | 0.0013797 |  |  |  | 5 |  | 1/2" |  | 1" | 1" | 1" | 1" | 1" | 1" | 1" | 1" | 1" | 1" | 1" | 1" | 1" | 1" | 1"
8 | Birthing and LDRP |  |  | 1 |  | 50 | 0 | 0 | [41 empty] | 50 |  |  | 0.016679 | 0.0036792 | 0.001717 |  |  |  | 5 |  | 1/2" |  | 1" | 1" | 1" | 1" | 1" | 1" | 1" | 1" | 1" | 1" | 1" | 1" | 1" | 1" | 1"
9 | Patient isolation room |  | 0.5 |  |  | 25 | 0 | 0 | [41 empty] | 60 |  |  | 0.024007 | 0.0055801 | 0.0024528 | 0.00067452 | [6 empty] | 1" | 1" | 1" | 1" | 1" | 1" | 1" | 1" | 1" | 1" | 1" | 1" | 1" | 1" | 1"
[50 empty] | 70 |  |  | 0.032684 | 0.007573 | 0.0033419 | 0.00088914 |  |  | 5 |  | 1/2" |  | 1" | 1" | 1" | 1" | 1" | 1" | 1" | 1" | 1" | 1" | 1" | 1" | 1" | 1" | 1"
Other Patient Rooms
[16 empty] | Temperature correction factor |  |  |  |  | weight of water vapor in air | [28 empty] | 80 |  |  | 0.042679 | 0.0099645 | 0.0043844 | 0.0011651 |  |  | 5 |  | 1/2" |  | 1" | 1" | 1" | 1" | 1" | 1" | 1" | 1" | 1" | 1" | 1" | 1" | 1" | 1" | 1"
1 | Anesthesia workroom |  |  | 1.5 |  | 10 | 0 | 0 | [7 empty] | intake temp |  |  |  |  | temp | [28 empty] | 90 |  |  |  | 0.01254 | 0.0055495 | 0.0014717 |  |  | 5 |  | 1/2" |  | 1 1/4" | 1 1/4" | 1 1/4" | 1 1/4" | 1 1/4" | 1 1/4" | 1 1/4" | 1 1/4" | 1 1/4" | 1 1/4" | 1 1/4" | 1 1/4" | 1 1/4" | 1 1/4" | 1 1/4"
2 | Respirator care |  |  | 1.5 |  | 10 | 0 | 0 | [7 empty] | deg C | deg F | factor |  |  | deg C | deg F | 0% | 10% | 20% | 160 1: 30%; A-REN-Q-200P-SS-N-200 2: 40%; Quad, 20 Hp 3: 50%; 260 4: 60%; 20 5: 70%; 45810 6: 80%; 195.3 7: 90% | 100 |  |  |  | 0.015497 | 0.0068372 | 0.0018396 | 0.00070949 | [5 empty] | 1 1/4" | 1 1/4" | 1 1/4" | 1 1/4" | 1 1/4" | 1 1/4" | 1 1/4" | 1 1/4" | 1 1/4" | 1 1/4" | 1 1/4" | 1 1/4" | 1 1/4" | 1 1/4" | 1 1/4"
workroom
3 | Nursery workroom |  |  | 1.5 |  | 10 | 0 | 0 | [6 empty] | 60 | -46 | -50 | 0.773 | temp: | 4 | -1 | 30 | 0 | 3 | 5 | 160 1: 7; A-REN-Q-200P-SS-N-200 2: 9; Quad, 20 Hp 3: 12; 260 4: 14; 20 5: 17; 45810 6: 19; 195.3 7: 21 | 110 |  |  |  | 0.018733 | 0.0082782 | 0.0022075 | 0.00085848 |  | 5 |  | 1/2" |  | 1 1/4" | 1 1/4" | 1 1/4" | 1 1/4" | 1 1/4" | 1 1/4" | 1 1/4" | 1 1/4" | 1 1/4" | 1 1/4" | 1 1/4" | 1 1/4" | 1 1/4" | 1 1/4" | 1 1/4"
4 | Equipment repair |  |  | 1.5 |  | 10 | 0 | 0 | [6 empty] | 0.981 | -40 | -40 | 0.792 | RH: | 1 | 4 | 40 | 0 | 4 | 7 | 160 1: 10; A-REN-Q-200P-SS-N-200 2: 14; Quad, 20 Hp 3: 16; 260 4: 18; 20 5: 20; 45810 6: 22; 195.3 7: 24 | 120 |  |  |  | 0.02229 | 0.0098725 | 0.0026368 | 0.0010118 |  | 5 |  | 1/2" |  | 1 1/4" | 1 1/4" | 1 1/4" | 1 1/4" | 1 1/4" | 1 1/4" | 1 1/4" | 1 1/4" | 1 1/4" | 1 1/4" | 1 1/4" | 1 1/4" | 1 1/4" | 1 1/4" | 1 1/4"
5 | Med. Laboratory3 |  |  |  | 1.5 | 25 | 0 | 0 | [7 empty] | -34 | -30 | 0.811 | gr/lb: | 0 | 10 | 50 | 0 | 6 | 10 | 160 1: 14; A-REN-Q-200P-SS-N-200 2: 20; Quad, 20 Hp 3: 26; 260 4: 32; 20 5: 38; 45810 6: 42; 195.3 7: 48 | 130 |  |  |  | 0.026153 | 0.011589 | 0.0030967 | 0.0011957 | [5 empty] | 1 1/4" | 1 1/4" | 1 1/4" | 1 1/4" | 1 1/4" | 1 1/4" | 1 1/4" | 1 1/4" | 1 1/4" | 1 1/4" | 1 1/4" | 1 1/4" | 1 1/4" | 1 1/4" | 1 1/4"
6 | Autopsy |  |  | 1 |  | 100 | 0 | 0 | [5 empty] | at 60 °F: | 0.981 | -28 | -20 | 0.83 |  |  | 18 | 60 | 0 | 8 | 16 | 160 1: 22; A-REN-Q-200P-SS-N-200 2: 30; Quad, 20 Hp 3: 39; 260 4: 48; 20 5: 54; 45810 6: 62; 195.3 7: 70 | 140 |  |  |  | 0.030323 | 0.013429 | 0.0035872 | 0.0014104 | [5 empty] | 1 1/4" | 1 1/4" | 1 1/4" | 1 1/4" | 1 1/4" | 1 1/4" | 1 1/4" | 1 1/4" | 1 1/4" | 1 1/4" | 1 1/4" | 1 1/4" | 1 1/4" | 1 1/4" | 1 1/4"
7 | Sterile supply |  |  | 1 |  | 10 | 0 | 0 | [7 empty] | -23 | -10 | 0.849 |  |  | 22 | 70 | 0 | 11 | 21 | 160 1: 34; A-REN-Q-200P-SS-N-200 2: 44; Quad, 20 Hp 3: 55; 260 4: 66; 20 5: 78; 45810 6: 88; 195.3 7: 100 | 150 |  |  |  | 0.03483 | 0.015422 | 0.0041084 | 0.0015943 | [5 empty] | 1 1/4" | 1 1/4" | 1 1/4" | 1 1/4" | 1 1/4" | 1 1/4" | 1 1/4" | 1 1/4" | 1 1/4" | 1 1/4" | 1 1/4" | 1 1/4" | 1 1/4" | 1 1/4" | 1 1/4"
8 | Plaster room |  |  | 1 |  | 50 | 0 | 0 | [5 empty] | total correction difference: | 0 | -18 | 0 | 0.867 |  |  | 27 | 80 | 0 | 16 | 30 | 160 1: 46; A-REN-Q-200P-SS-N-200 2: 62; Quad, 20 Hp 3: 78; 260 4: 92; 20 5: 108; 45810 6: 125; 195.3 7: 140 | 160 |  |  |  | 0.039858 | 0.017538 | 0.0046603 | 0.0018163 | [5 empty] | 1 1/4" | 1 1/4" | 1 1/4" | 1 1/4" | 1 1/4" | 1 1/4" | 1 1/4" | 1 1/4" | 1 1/4" | 1 1/4" | 1 1/4" | 1 1/4" | 1 1/4" | 1 1/4" | 1 1/4"
9 | Pharmacy |  |  | 1 |  | 10 | 0 | 0 | [7 empty] | -9 | 10 | 0.886 |  |  | 32 | 90 | 0 | 21 | 42 | 160 1: 65; A-REN-Q-200P-SS-N-200 2: 85; Quad, 20 Hp 3: 108; 260 4: 128; 20 5: 158; 45810 6: 173; 195.3 7: 195 | 170 |  |  |  | 0.045009 | 0.019868 | 0.0041084 | 0.0020504 | [5 empty] | 1 1/4" | 1 1/4" | 1 1/4" | 1 1/4" | 1 1/4" | 1 1/4" | 1 1/4" | 1 1/4" | 1 1/4" | 1 1/4" | 1 1/4" | 1 1/4" | 1 1/4" | 1 1/4" | 1 1/4"
[16 empty] | -5 | 20 | 0.905 |  |  | 38 | 100 | 0 | 29 | 58 | 160 1: 87; A-REN-Q-200P-SS-N-200 2: 116; Quad, 20 Hp 3: 147; 260 4: 176; 20 5: 208 | 180 |  |  |  | 0.05016 | 0.022198 | 0.0058867 | 0.0022987 | [5 empty] | 1 1/4" | 1 1/4" | 1 1/4" | 1 1/4" | 1 1/4" | 1 1/4" | 1 1/4" | 1 1/4" | 1 1/4" | 1 1/4" | 1 1/4" | 1 1/4" | 1 1/4" | 1 1/4" | 1 1/4"
Future Expansion | [7 empty] | 0 | [7 empty] | -1 | 30 | 0.925 | [31 empty] | 190 |  |  |  | 0.056073 | 0.024773 | 0.0052735 | 0.0025613 | [5 empty] | 1 1/4" | 1 1/4" | 1 1/4" | 1 1/4" | 1 1/4" | 1 1/4" | 1 1/4" | 1 1/4" | 1 1/4" | 1 1/4" | 1 1/4" | 1 1/4" | 1 1/4" | 1 1/4" | 1 1/4"
[16 empty] | 4 | 40 | 0.943 | [31 empty] | 200 |  |  |  | 0.061987 | 0.027349 | 0.0073584 | 0.002838 | [5 empty] | 1 1/4" | 1 1/4" | 1 1/4" | 1 1/4" | 1 1/4" | 1 1/4" | 1 1/4" | 1 1/4" | 1 1/4" | 1 1/4" | 1 1/4" | 1 1/4" | 1 1/4" | 1 1/4" | 1 1/4"
[7 empty] | PEAK CALCULATED DEMAND IN SCFM BASED ON FREE AIR SCFM @ 50PSI: | 0 | [7 empty] | 10 | 50 | 0.962 |  |  | moisture content of air | [28 empty] | 220
| NOTES: | [14 empty] | 18 | 60 | 0.981 |  |  | gr/lb | vol % | [27 empty] | 530 | [8 empty] | 0.01 | 0.007 | [15 empty] | 6" | 6"
| 1. The SCFM above is based on a peak OUTLET demand of 50 psi. Air compressors operate at 100 psi. When sizing a | [14 empty] | 22 | 70 | 1 |  | 0 | 0 | 0 | 400
| compressor, you MUST figure the compressor capacity for operation at 100 psi. | [14 empty] | 27 | 80 | 1.019 |  | 0 | 0.008 | 0.0001 | 366 | [26 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28
| 2. You need to consider several environmental factors when sizing the compressors. These include altitude, intake air | [14 empty] | 32 | 90 | 1.038 |  |  | 0.01 | 0.0002 | 333
| temperature, and relative humidity. Variance among these factors has considerable effect on compressor selection. | [14 empty] | 38 | 100 | 1.057 |  |  | 0.02 | 0.0004 | 300
| 3. Air outlets in labs used for analysis, research or teaching should be supplied by a separate compressed air system, | [14 empty] | 43 | 110 | 1.076 |  |  | 0.025 | 0.0006 | 266 | [26 empty] | 1: 530
not the medical air system.
[16 empty] | 49 | 120 | 1.095 |  |  | 0.03 | 0.0008 | 233 | [26 empty] | 1: 220
[7 empty] | Altitude above sea level, ft: | 0 | [12 empty] | 0.035 | 0.0008 | 200 | [26 empty] | 1: 200
[21 empty] | 0.04 | 0.001 | 150 | [26 empty] | 1: 190
[7 empty] | Intake air temperature, °F: | 60 | [12 empty] | 0.06 | 0.0015 | 100 | [26 empty] | 1: 180
[21 empty] | 0.08 | 0.002 | 90 | [26 empty] | 1: 170
[7 empty] | Relative Humidity: | 0% | [12 empty] | 0.1 | 0.003 | 80 | [26 empty] | 1: 160
[21 empty] | 0.15 | 0.004 | 70 | [26 empty] | 1: 150
[7 empty] | PEAK CALCULATED DEMAND IN SCFM: | 0 | [12 empty] | 0.2 | 0.006 | 60 | [26 empty] | 1: 140
[7 empty] | Adjusted for altitude, highest intake air temperature, | [13 empty] | 0.3 | 0.008 | 50 | [26 empty] | 1: 130
[7 empty] | and highest relative humidity expected. | [13 empty] | 0.45 | 0.01 | 40 | [26 empty] | 1: 120
[21 empty] | 0.6 | 0.015 | 35 | [26 empty] | 1: 110
[21 empty] | 0.8 | 0.02 | 30 | [26 empty] | 1: 100
| RECIPROCATING | [6 empty] | Amps | Total | [11 empty] | 1 | 0.03 | 25 | [26 empty] | 1: 90
| COMPRESSORS | System |  | Horsepower |  | System Capacity | Btu/h | @ 208/460V | Noise | Dimensions (in) |  | Catalog | Sugg'd | [7 empty] | 1.5 | 0.04 | 20 | [26 empty] | 1: 80
|  | Model # |  | each | total | SCFM @ 100PSI | each pump | each pump | level (dB) | L x W x H |  | Cuts: | Specs: | [7 empty] | 2 | 0.05 | 17 | [26 empty] | 1: 70
| Recommended | [19 empty] | 3 | 0.06 | 13 | [26 empty] | 1: 60
| System: | [19 empty] | 4 | 0.08 | 10 | [26 empty] | 1: 50
| The compressor models specified are sized according to the calculated demand in SCFM adjusted to the indicated altitude, | [19 empty] | 5 | 0.1 | 8 | [26 empty] | 1: 45
| inlet temperature, and relative humidity. | [19 empty] | 6 | 0.15 | 6 | [26 empty] | 1: 40
| The Btu/hr and amperage listed are for each pump. | [19 empty] | 8 | 0.2 | 5 | [26 empty] | 1: 35
| The noise level indicated is for the complete system. | [19 empty] | 10 | 0.25 | 4 | [26 empty] | 1: 30
[21 empty] | 13 | 0.3 | 3 | [26 empty] | 1: 25
| SCROLL | [6 empty] | Amps | Total | [11 empty] | 17 | 0.4 | 2 | [26 empty] | 1: 20
| COMPRESSORS | System |  | Horsepower |  | System Capacity | Btu/h | @ 208/460V | Noise | Dimensions (in) |  | Catalog | Sugg'd | [7 empty] | 20 | 0.5 | 1.5 | [26 empty] | 1: 15
|  | Model # |  | each | total | SCFM @ 100PSI | each pump | each pump | level (dB) | L x W x H |  | Cuts: | Specs: | [7 empty] | 25 | 0.6 | 1 | [26 empty] | 1: 10
| Recommended | [19 empty] | 30 | 0.7 | 0.8 | [26 empty] | 1: 5
| System: | [19 empty] | 35 | 0.8 | 0.6
[21 empty] | 40 | 0.9 | 0.45
|  |  | INTAKE LINE SIZING | [17 empty] | 50 | 1 | 0.3
|  |  |  | Length, Ft: | [16 empty] | 60 | 1.25 | 0.2
|  |  |  | Line Dia: | [16 empty] | 70 | 1.5 | 0.15
[21 empty] | 80 | 1.66 | 0.1
| For all length input, enter the actual, measured run of pipe. The equivalent length of pipe (due to additional friction loss | [19 empty] | 90 | 1.83 | 0.08
| through fittings, filters, valves, etc.) is automatically calculated and used to determine the proper pipe diameter. | [19 empty] | 100 | 2 | 0.06
[21 empty] | 150 | 3 | 0.04
| ZONE PIPE SIZING | [19 empty] | 200 | 4 | 0.035
|  | Zone #1 | Zone #2 | Zone #3 | Zone #4 | Zone #5 | Zone #6 | Zone #7 | Zone #8 | Zone #9 | Zone #10 | [9 empty] | 233 | 5 | 0.03
| Flow SCFM: | [19 empty] | 266 | 6 | 0.025
| Length, Ft: | [19 empty] | 300 | 6.5 | 0.02
| Zone Dia. | [19 empty] | 333 | 7 | 0.01
[21 empty] | 366 | 8 | 0.008
[21 empty] | 400 | 9 | 0
For all length input, enter the actual, measured run of pipe. The equivalent length of pipe (due to additional friction loss
through fittings, filters, valves, etc.) is automatically calculated and used to determine the proper pipe diameter.
BRANCH PIPE SIZING
[5 empty] | Branch #1 | Branch #2 | Branch #3
Flow SCFM:
Length, Ft:
Branch Dia.
For all length input, enter the actual, measured run of pipe. The equivalent length of pipe (due to additional friction loss
through fittings, filters, valves, etc.) is automatically calculated and used to determine the proper pipe diameter.
RISER PIPE SIZING
[5 empty] | Riser #1: | Riser #2:
Flow SCFM:
Length, Ft:
Riser Dia.